The procedures for updating the software

Step 1: Execute ‘SCCMPPT.rar’ to install the Reflash Software.

Note: Reflash tool can only be executed in OS of windows

Step 2: Connect the AXPERT and the PC by a RS232 to RJ45 cable

Note: The COM port must be COM1.

Step 3: Make sure all application communication software using the COM port1 is closed. The application software include some monitoring software

Step 4: Connect the DC power or battery (must be more than start up voltage, 46V) to the battery connector, then switch on the AXPERT. Connect the DC power or PV panel (must be 6V higher than battery voltage)to the PV connector.

Step 5: Run the programming application “IapProgram.exe”

Step 6: Click button ,

Figure 2

Select the MCU configuration file “SCC.m08” in release firmware package, by double clicking it.

Figure 3

Step 7: Click button ,

Figure 4

Select the firmware file in release firmware package (SCCMPPT.s19), by double clicking it.

Figure 5

Step 8: Click button , and then wait till programming complete. Please DON’T press “Stop” button!

Figure 6

Step 9:	When the processing bar is up to 100%, below dialog will pop-up to remind you the programming is successful! Now the software is updated completely!

Application Notes:

- If update tool remind “time out” as below, please check the communication and PV/battery source, make sure communicate fine and inverter work normal. Then cut-off all source and try again from step 4.

- Com port inquiry.

Computer management>>Device manage>>Ports(COM&LPT)

- Com port change

If the com port most than com1, change it to be COM1.